# PACKAGED METERING MANHOLES

SECTION 11210

METERING MANHOLES

PART 1	GENERAL

  - SECTION INCLUDES

- Metering manholes.

  - RELATED SECTIONS

  - REFERENCES

- ASTM C 581 – Practice for Determining Chemical Resistance of Chemical Thermosetting Resins Used in Glass-Fiber Reinforced Structures Intended for Liquid Service.

- ASTM D 638 – Standard Test Method for Tensile Properties of Plastics.

- ASTM D 695 – Standard Test Methods for Compressive Properties of Rigid Plastics.

- ASTM D 790 – Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

- ASTM D 2583 – Standard Test Method for Indentation Hardness of Rigid Plastics by Means of a Barcol Impressor.

- ASTM D 2584 – Standard Test Method for Ignition Loss of Cured Reinforced Resins.

- ASTM D 3753 – Standard Specification for Glass-Fiber Reinforced Polyester Manholes.

- AASHTO H-20 – Axial Loading.

  - SUBMITTALS

- Submit under provisions of Section 01300.

- Product Data:  Test results of representative fiberglass reinforced plastic laminate.

- Shop Drawings:  Show:

  - Critical dimensions, jointing and connections, fasteners and anchors.

  - Materials of construction.

  - Sizes, spacing, and location of structural members, connections, attachments, openings, and fasteners.

  - Colors.

- Samples:  8-inch square sample of representative fiberglass reinforced plastic laminate, upon request.

- Manufacturer’s installation instructions.

  - DELIVERY, STORAGE, AND HANDLING

- Store products indoors or in weather protected area until installation.  Protect from construction traffic and damage.

- During the loading, unloading, and storage, care should be taken to ensure that the manhole is not dropped or otherwise damaged.

- The manhole should be stored on a smooth surface free of sharp objects.

- Nylon or fabric slings should be used in conjunction with a spreader bar to lift or move the manhole.

- UNDER NO CIRCUMSTANCES SHOULD CABLES OR CHAINS BE USED.

- If the manhole is stored horizontally, the manhole should be placed in such a way as to avoid damage to the flume, cover, and end adapters.

PART 2	PRODUCTS

  - MANUFACTURER

- The product shall be manufactured by TRACOM, Inc.; 6575-A Industrial Way, Alpharetta, Georgia 30004; Toll-Free Voice (877) 435-8637, Toll-Free Fax (866) 435-8637, www.tracomfrp.com.

- Requests for substitution must be made in writing and received by the engineer’s office a minimum of ten (10) business days before bid opening.

- Substitutions:  Manufacturers not pre-approved shall not be allowed.

- Fiberglass tanks modified for flume installation shall not be allowed.

- Warranty:  Manholes shall be warranted to be free of defects in workmanship and materials for a period of (2) two years from shipment.

2.2	METERING MANHOLES

- Configuration:

  - Size: _______ (select 48, 60, or 72) INCH DIA. X ______ FEET ______ INCHES H.

    - The manhole height shall be as measured from:

      - Dome top manholes:

        - Inlet invert to surface grade plus 12 inches

        - Inlet invert to surface grade plus 18 inches when using a gooseneck vent

      - Aluminum hatch:  Inlet invert to surface grade.

      - H-20 manholes:  Inlet invert to surface grade minus 12 inches (typical) [manhole bottom to reducer top shoulder].

- Construction:

  - One-piece construction.

  - Two-piece construction.  Sectioning of the metering manhole into two sections for shipment to the job site (field assembly by others).  Includes:  T-304 stainless steel connection hardware, predrilled external manhole barrel connection flanges, and urethane sealant (OPTIONAL).

- Materials:

  - Fiberglass reinforced plastic, complying with ASTM D 3753, latest edition.

  - Factory-assembled, ready for installation except for field-installed equipment.

  - The exterior surface shall be relatively smooth with no sharp projections.  The surface shall be free of blisters larger than 1/2 inch in diameter, delamination and fiber show.

  - The interior surfaces shall be resin rich and unpigmented to allow for visual inspection of the manhole laminate.  There shall be no exposed fibers.  Additionally the interior surface shall be smooth for improved corrosion resistance and reduced sludge build-up.  The surface shall be free of crazing, delamination, blisters larger than 1/2 inch in diameter, and wrinkles of 1/8 inch or greater in depth.

  - Minimum 1/2 inch wall thickness.

  - Integral fiberglass ladder bolted and glassed to the manhole wall with 1-1/2 inch diameter pultruded fiberglass rungs with a photoluminescent high visibility non-slip top surface and reinforced with threaded T-304 5/16 inch diameter stainless steel rods and solid 1-1/4 inch diameter pultruded fiberglass spacers.

  - Inlet and outlet end connections molded to the flume and laminated to the manhole barrel.  The end connections shall be provided with:

    - ________ inch diameter PVC or fiberglass pipe stubs with flexible PVC boots and stainless steel bands to connect to __________ inch diameter, __________ pipe.

    - ________ inch, ANSI 150 lb. flat-faced fiberglass flanges (OPTIONAL – in lieu of pipe stubs).

  - A 3/4 inch thick expanded polystyrene bead board shall be supplied to place under the manhole on the concrete slab.

  - A 4 inch wide FRP integral mounting flange shall be molded to the base of the manhole barrel for anchoring to the manhole to the concrete slab.

  - An OSHA approved “Confined Space Entry” sign shall be applied to the interior surface of the manhole above the first ladder rung (H-20 type) or on the underside of the manhole top (dome top and aluminum hatch types).

  - One (1) 2 inch NPT coupling to facilitate the installation of sample or bubble tubing, electrical power, or other cabling into the manhole.  Run sample lines and electrical lines in separate conduits or cross-talk may occur across unshielded electrical lines.

- Materials:

  - The resins used shall be unsaturated, supplier certified, isophthalic polyester resins.  Mixing lots of resin from different manufacturers or “odd-lotting” of resins shall not be permitted.  Quality assurance records on the resin shall be maintained.

  - The manhole interior shall be provided with a resin rich, corrosion resistant interior surface.  The interior surface shall be unpigmented to allow for visual inspection for voids, inclusions, and defects as well as for verification that “odd-lotting” has not occurred.

  - 15 mil isophatlic U.V. resistant gel coat on all exterior surfaces

  - Reinforcing materials shall be high performance commercial grade with a coupling agent that will provide a suitable bond between the glass reinforcement and the resin.

  - The manhole laminate shall consist of multiple layers of glass matting and resin.  The surface exposed to the sewer / chemical environment shall be resin rich and shall have no exposed fibers.

  - The flume laminate shall be a minimum of 3/16 thick with a 15 mil isophthalic U.V. resistant gel coat, with those portions of the flume extending outside the manhole sufficiently thickened and reinforced as necessary to withstand the forces of the intended application.

- Material Properties:

  - Manhole Barrel and Reducer:

    - Flexural strength (ASTM D 790):		15,400 PSI (reducer - hoop).

17,200 PSI (reducer - axial).

22,500 PSI (reducer - hoop).

14,300 PSI (reducer - axial).

    - Compressive Strength (ASTM D 695):	18,900 PSI (barrel)

    - Barrel Stiffness (ASTM D2412):

Manhole Length (ft.)			PSI

  - 0.72

  - 1.26

  - 2.01

  - 3.02

26-35				5.24

  - Flume:

    - Tensile strength (ASTM D 638):		14,000 PSI.

    - Flexural strength (ASTM D 790):		27,000 PSI.

    - Flexural modulus (ASTM D 790):		1,000,000 PSI.

    - Barcol hardness (ASTM D 2583):		50.

- Top Style:

  - Dome Top:  (48, 60, and 72 inch diameter manholes)

    - A fully opening dome top cover rated for 1,000 lb. static top load with a solid FRP hinge block, neoprene gasket for sealing, and stainless steel hardware (consisting of a piano hinge, lockable hasp, and cover support bar with locking pin on a retaining chain).

  - Aluminum Hatch:  (48, 60, and 72 inch diameter manholes)

    - ________  W x _______ D, (select non-watertight or watertight) aluminum hatch rated for a 300 P.S.F. pedestrian load.  The hatch shall be mounted to a reinforced fiberglass cover and shall be fabricated from reinforced 1/4 inch thick aluminum diamond plate with T-316 stainless steel hardware.  The hatch shall be provided with an automatic locking hold open arm, a stainless steel, recessed lift handle, and a staple for a user supplied padlock.  The hatch shall be warranted against defects in materials and workmanship by the hatch manufacturer (10) years.

    - Aluminum Hatch Options:

      - Compression spring assist.

      - Hatch safety net fall prevention, meeting OSHA standard 1926.502 (c) (4) (i) drop test.

        - Removable safety net.

        - Hinged safety net with 90 degree rotating frame and hold open rod.

      - Insulation, factory applied, 1 inch thick.

      - Safety chain and posts.

      - Slip resistant surface:  The cover surface of the hatch shall be manufactured of a slip resistant plate which has a minimum 0.6 coefficient of friction (in lieu of standard diamond plate).

      - Special engraving.

  - H-20 Highway Loading:  (48 and 60 inch diameter manholes)

    - A purposed-built, 31-3/4 (OPTIONAL 22-1/2) inch opening H-20 highway loading reducer designed and certified to withstand a 16,000 pound vertical dynamic wheel load and be fully compliant with AASHO H-20.  Grade rings, cover, and frame by contractor.

- Flume Type and Size:

  - _______________ (specify size and style - Parshall, Palmer-Bowlus, Trapezoidal, HS/H-flume, or Cutthroat)  flume with integral inlet and outlet end connections.

2.3	MANHOLES OPTIONS (select all that apply)

- Coupling:  additional 2 inch NPT coupling (for signal, power, and sampling lines).

- Anchor Bolts:  T-304 stainless steel anchor bolts (1/2 inch diameter x 4-1/2 inches long – minimum).

- Instrument Mounting Plate:  18 inches W x 18 inches H fiberglass mounting plate.

- Instrument Shelf:  18 inches W x 12 inches D fiberglass shelf.

- Light:  100 watt, NEMA 4X non-metallic incandescent light with weatherproof single toggle switch (mounted, not wired).

- Outlet:  15 A duplex GFCI outlet with weatherproof cover (not wired).

- Platform:  An intermediate platform ________ feet from the top (Dome top and Aluminum Hatch types) or shoulder (H-20 type) of the manhole constructed of open-cell fiberglass grating, with a stainless steel piano hinge, and mounted to a fiberglass support flange.

- Half-diameter.

- Full-diameter.

- Vent:

- Screened gooseneck vent, 4 inch diameter.

- In-line intake or exhaust fan with screened gooseneck vent, 4 inch diameter, and weatherproof single toggle switch (mounted, not wired).

2.4	FLUME AND MEASUREMENT OPTIONS (select all that apply)

- Attached stilling well:

- 8 inch diameter, with 2 inch opening.

- 12 inch diameter, with 2 inch opening.

- Laminated (OR) Molded-in, high visibility staff gauge:

- Graduated in 1/10 foot and 1/100 foot increments.

- Graduated in 1/10 foot, 1/100 foot, and MGD increments (3 inch - 72 inch Parshall flumes only).

- Graduated in 1/10 foot, 1/100 foot, and GPM increments (Small-Extra Large Trapezoidal flumes only).

- Graduated in 2mm increments.

- Ultrasonic mounting bracket:

- Fixed position, horizontally adjustable, T-304 stainless steel.

- Horizontally and vertically adjustable stainless steel.

- Vertically adjustable, over-channel, 304 stainless steel.

- Removable T-316 stainless steel bubble tube, for 1/8 inch O.D. bubble line.

- Removable T-316 stainless steel sample tube, for 3/8 inch O.D. sample line.

- Removable T-316 stainless steel probe carrier in molded-in cavity (specify length and O.D. of probe).

- 2 inch diameter probe well with 2 inch opening to flume.

- Removable open cell fiberglass grating over the flume.

- Removable flat fiberglass cover with T-304 stainless steel bolt hardware over the flume.

- Chemical or temperature resistant service (the standard flexible boots are PVC, ensure that either the chemical or temperature is compatible with PVC or that alternate end connects are provided):

  - Gel coat only.

  - Gel coat and resin (required for temperature service).

  - Maximum temperature: ________ ° F.

  - Chemical(s) and concentration(s): __________________________________________.

PART 3	EXECUTION

  - EXAMINATION

- Verify that the flume dimensions are correct and project conditions are suitable for installation.  Do not proceed with installation until condition deficiencies have been corrected.

  - INSTALLATION

- Install products in accordance with engineer’s instructions, plans, blueprints, etc, local codes, and in a manner consistent with the installation instruction and recommendation of the manufacturer.

- Ensure that the product is installed plumb and true, free of twist or warp, within the tolerances specified by the manufacturer and as indicated in the contract documents.

- Nylon or fabric slings should be used in conjunction with a spreader bar to lift or move the manhole.

UNDER NO CONDITIONS SHOULD CHAINS OR CABLES BE USED.

- Excavate an area large enough to contain the manhole and the concrete pad while allowing for sufficient space to allow for a safe work environment.

- Follow all OSHA requirements for open trench construction.

- Pour a pad of sufficient width and length to support all of the manhole, the flume, and the connecting piping.  The thickness of the pad shall be ____________ and shall be sized to ensure that proper loading is observed and that the manhole will not float.  The surface of the pad should be level to within 1/8 inch.

- Clean the concrete slab of all sharp objects and debris before laying the foam pad provided with the manhole.

- If PVC boots are provided, install them on the manhole pipe stubs before lowering the manhole into the opening.

- Lower the manhole onto the pad.

- Drill holes in the base mounting flange, foam, and concrete pad to accept the stainless steel anchor bolts (supplied by others unless indicated in 2.2.E).

- Check to ensure that the flume is level from side to side and from front to back, adjust the pad and anchor bolts, shimming if necessary.

- Connect and secure piping.

DO NOT LUBRICATE THE PVC BOOTS.

- Grout the areas between the flume and the concrete pad outside of the manhole.

- Backfill with pea gravel, 1/4 to 3/4 inch in diameter, using uniform lifts of no more than 12 inches.

WARNING:  METERING MANHOLES MAY BE CLASSIFIED AS CONFINED SPACE ENTRY LOCATIONS.  CONSULT ALL APPROPRIATE LOCAL, STATE, AND FEDERAL REGULATIONS BEFORE ENTERING.

- For additional installation instructions refer to latest revision of document MH-I.

  - ADJUST AND CLEAN

- Clean surfaces in accordance with the manufacturer’s instructions.

- Remove trash and debris, and leave the site in a clean condition.

#### END OF SECTION

Document:  MH-S

Date:	5-23-14

By:	Matt Kazmier